PRICE ESTIMATE FOR THE TAPE VAULT AIR-CONDITIONING USING LOCAL AIR HANDLING UNITS

The price estimate includes the air-conditioning system installed in the Tape Vault area with all the necessary piping works (chilled water, condensate drains), electrical connections and controls and alarms. What is not included is the works related to civil engineering, like installation of the false floor, holes etc.

# 1. AIR HANDLING UNITS

The units (6) will be installed along the walls of the computer room (one in the middle). The supply of air will be from the false floor and the exhaust directly from the top of the unit. No ducting is used.

The units consist of :

- filter

- cooling coil (CW)

- integrated controls

- humidification

# 25000CHF

- support structures

- works

## 30000CHF

180000CHF

# 2. CHILLED WATER

Chilled water will be supplied from the existing plant. The pipes will run along the computer room walls forming a closed loop. The pipes will be insulated and covered by aluminium sheet.

The pipes :

- DN 150		  40m x 250CHF			10000CHF

- DN 100		140m x 170CHF			23800CHF

- DN 65			  60m x 115CHF			  6900CHF

- pipe accessories +30%					12300CHF

-	works								27000CHF

80000CHF

# 3. DRAINS

Drains are installed in the false floor to evacuate the possible condensate from the units.

The pipes in plastic:

- DN 50			25m

- DN 32		 	25m

- pipe accessories

-	works

# 10000CHF

# 4. ELECTRICITY AND CONTROLS

- supply cabinet

- cabling

- alarms

50000CHF

# 5. RESERVE

- 10% of the total

30000CHF

# 6. TOTAL PRICE

- total for air-conditioning

350 000CHF